## house
https://www.engineeringtoolbox.com/heat-loss-transmission-d_748.html
https://www.heatgeek.com/heat-losses/
outside temperature C | 6.2
req’d inside temperature C | 18
heating power (W) | 2881.1659
| HDD in year | 3600 | C-days
| average delta T | 9.8563 | C |  |  | 0.0036 | Watt-hour to MJ
| 1 year | 8766 | hours
| energy in year | 90.9227 | GJ | [7 empty] | 4.285
|  | 25.2563 | MJ/HDD
location | qty | RSI m2·K/W | U W/m2·K | Area m2 | Heat transfer W/K | Design ΔT K | Heating power W | yearly Energy transfer MJ | %
Windows | 17 | 0.35714 | 2.8 | 25.45 | 71.26 | 11.8 | 840.868 | 26535.776 | 29.18%
Main floor brick | 1 | 3.56 | 0.2809 | 122 | 34.2697 | 11.8 | 404.382 | 12761.3261 | 14.04%
Main floor walls | 1 | 3.56 | 0.2809 | 102.9 | 28.9045 | 11.8 | 341.073 | 10763.4464 | 11.84%
doors | 4 | 0.38462 | 2.6 | 9.86 | 25.636 | 11.8 | 302.5048 | 9546.3255 | 10.5%
Attic | 1 | 8.54 | 0.1171 | 160.3 | 18.7705 | 11.8 | 221.4918 | 6989.7497 | 7.688%
Foundation interior | 1 | 2.7 | 0.37037 | 40.9 | 15.1481 | 11.8 | 178.7481 | 5640.8626 | 6.204%
Main floor walls buffered | 1 | 2.78 | 0.35971 | 33.4 | 12.0144 | 11.8 | 141.7698 | 4473.9141 | 4.921%
Foundation crawlspace | 1 | 1.77 | 0.56497 | 19.7 | 11.1299 | 11.8 | 131.3333 | 4144.5648 | 4.558%
foundation slab | 1 | 10 | 0.1 | 64.8 | 6.48 | 11.8 | 76.464 | 2413.0203 | 2.654%
crawlspace slab | 1 | 10 | 0.1 | 58.3 | 5.83 | 11.8 | 68.794 | 2170.9735 | 2.388%
Floor over garage | 1 | 5.32 | 0.18797 | 28.3 | 5.3195 | 11.8 | 62.7707 | 1980.8919 | 2.179%
foundation pony wall | 1 | 2.95 | 0.33898 | 11.5 | 3.8983 | 11.8 | 46 | 1451.6496 | 1.597%
foundation header | 1 | 2.51 | 0.39841 | 9 | 3.5857 | 11.8 | 42.3108 | 1335.2259 | 1.469%
Floor back cantilever | 1 | 5.3 | 0.18868 | 8.7 | 1.6415 | 11.8 | 19.3698 | 611.2648 | 0.6723%
air infiltration | [6 empty] | 3.2857 | 103.6898 | 0.114%
leaks
volume of house | 626.0139 | m3 – back calculated from EqLA and ACH |  |  |  |  | H i = Cp ρ n V (t i - t o ) |  |  | https://www.engineeringtoolbox.com/heat-loss-buildings-d_113.html
air changes per hour | 1.75 | measured 1.75 at 50 Pa |  |  |  | Cp | 0.7171 | kJ/kgK
equivalent leak area (EqLA) | 416 | cm^2 |  |  |  | ρ | 1.276 | kg/m3
cfm50 | 644.8013 | cubic feet per minute |  |  |  |  | 0.00027778 | hours/second
∆T | 11.8
rate of heat loss (watts) | 3.2857
Φ = A × U × ΔT
where Φ is the heat transfer in watts, U is the thermal transmittance, ΔT is the temperature differential across the structure, A is the area in square metres. https://en.wikipedia.org/wiki/Thermal_transmittance
Rate of heat loss (W/K) = V x ACH x ∆T x Kfactor
ACH – air changes per hour
Rate of heat loss per ˚C difference between inside and outside = V x ACH x Kfactor
Kfactor make the units work out
V is the volume of the room in cubic meters
∆T is the temperature difference in degrees C

## garage
https://www.engineeringtoolbox.com/heat-loss-transmission-d_748.html
desired temperature | 65 | °F | 18.3333 | C | [5 empty] | m2_per_sqft | 0.092903
design outside temperature | 6 | °F | -14.4444 | C | [5 empty] | RSI per R-value | 0.1761
heating power (W) | 772.0188 | [8 empty] | BTU per watt-hour | 3.4121
energy in one hour | 2634.2369 | BTU/hr
| HDD in year | 3600 | C-days
| average delta T | 9.8563 | C
| 1 year | 8766 | hours
| energy in year | 16.0086 | GJ
|  | 4.4468 | MJ/HDD
[7 empty] | total | 16008.5812
location | R-value | RSI m2·K/W | U W/m2·K | Area m2 | Heat transfer W/K | Design ΔT °C or K | Heating power W | Energy transfer MJ | %
R13 walls | 13 | 2.2893 | 0.43681 | 53.5122 | 23.3749 | 15 | 350.6235 | 7270.5279 | 45.42%
ceiling | 19 | 3.3459 | 0.29887 | 48.3096 | 14.4384 | 15 | 216.5766 | 4490.9328 | 28.05%
R7.5 wall | 7.5 | 1.3208 | 0.75715 | 14.8645 | 11.2546 | 15 | 168.8187 | 3500.6245 | 21.87%
window | 1.8929 | 0.33333 | 3 | 0.8 | 2.4 | 15 | 36 | 746.496 | 4.663%
assuming 26’x20’ footprint
Φ = A × U × ΔT
where Φ is the heat transfer in watts, U is the thermal transmittance, ΔT is the temperature differential across the structure, A is the area in square metres. https://en.wikipedia.org/wiki/Thermal_transmittance

## ICF house
https://www.engineeringtoolbox.com/heat-loss-transmission-d_748.html
https://www.heatgeek.com/heat-losses/
outside temperature C | -10
desired inside temperature C | 20
heating power (W) | 5686.207
| HDD in year | 3600 | C-days
| average delta T | 9.8563 | C
| 1 year | 8766 | hours
| energy in year | 58.9546 | GJ
|  | 16.3763 | MJ/HDD
location | qty | RSI m2·K/W | U W/m2·K | Area m2 | Heat transfer W/K | Design ΔT K | Heating power W | yearly Energy transfer MJ | %
Windows 1 | 25 | 0.44053 | 2.27 | 34.65 | 78.6555 | 30 | 2359.665 | 24465.0067 | 41.5% | windows avg U-factor
Floor header 1st floor | 1 | 3.87 | 0.2584 | 119.9 | 30.9819 | 30 | 929.4574 | 9636.614 | 16.35% | 2.272
Floor header 2nd floor | 1 | 3.87 | 0.2584 | 107.8 | 27.8553 | 30 | 835.6589 | 8664.1116 | 14.7%
Foundation interior | 1 | 4.41 | 0.22676 | 92.2 | 20.907 | 30 | 627.2109 | 6502.9224 | 11.03%
Attic | 1 | 6.85 | 0.14599 | 96.9 | 14.146 | 30 | 424.3796 | 4399.9673 | 7.463%
doors | 4 | 1 | 1 | 8.08 | 8.08 | 30 | 242.4 | 2513.2032 | 4.263%
Basement-1 pony wall | 1 | 3.52 | 0.28409 | 19.1 | 5.4261 | 30 | 162.7841 | 1687.7455 | 2.863%
Basement-1 header | 1 | 3.87 | 0.2584 | 13.5 | 3.4884 | 30 | 104.6512 | 1085.0233 | 1.84%
leaks
volume | 745.3589 | cubic meters
air changes per hour | 1.22 | measured 1.75 at 50 Pa
equivalent leak area (EqLA) | 345.3 | cm^2
cfm50 | 535.2161 | cubic feet per minute
∆T | 30
rate of heat loss (watts) | 6.9338
Φ = A × U × ΔT
where Φ is the heat transfer in watts, U is the thermal transmittance, ΔT is the temperature differential across the structure, A is the area in square metres. https://en.wikipedia.org/wiki/Thermal_transmittance