## house
https://www.engineeringtoolbox.com/heat-loss-transmission-d_748.html

heating power (W)	7574

	HDD in year	3600	C-days
	average delta T	9.86	C
	1 year	8766	hours
	energy in year	81	GJ
		22.52	MJ/HDD

location	qty	RSI / m2·K/W	U / W/m2·K	Area / m2	Heat / transfer / W/K	Design / ΔT / K	Heating / power / W	yearly / Energy / transfer / MJ	%
Windows	17	0.36	2.80	25.5	71.26	30	2138	22165	27%					4.28495559215388
Main floor brick	1	2.39	0.42	122.0	51.05	30	1531	15877	20%
Main floor walls	1	3.56	0.28	102.9	28.90	30	867	8990	11%
doors	4	0.38	2.60	9.9	25.64	30	769	7974	10%
Attic	1	8.54	0.12	160.3	18.77	30	563	5838	7%
Foundation interior	1	2.70	0.37	40.9	15.15	30	454	4712	6%
Main floor walls buffered	1	2.78	0.36	33.4	12.01	30	360	3737	5%
Foundation crawlspace	1	1.77	0.56	19.7	11.13	30	334	3462	4%
foundation slab	1	10.00	0.10	64.8	6.48	10	65	2016	2%
crawlspace slab	1	10.00	0.10	58.3	5.83	10	58	1813	2%
Floor over garage	1	5.32	0.19	28.3	5.32	30	160	1655	2%
foundation pony wall	1	2.95	0.34	11.5	3.90	30	117	1213	1%
foundation header	1	2.51	0.40	9.0	3.59	30	108	1115	1%
Floor back cantilever	1	5.30	0.19	8.7	1.64	30	49	511	1%
Φ = A × U × ΔT
where Φ is the heat transfer in watts,
U is the thermal transmittance,
ΔT is the temperature differential across the structure,
A is the area in square metres.
https://en.wikipedia.org/wiki/Thermal_transmittance

## garage
https://www.engineeringtoolbox.com/heat-loss-transmission-d_748.html
					m2_per_sqft	0.09290304
heating power (W)	772					RSI per R-value	0.1761
energy in one hour	2634	BTU/hr					assuming 26’x20’ footprint
					desired temperature °F	65
	HDD in year	3600	C-days					BTU per watt-hour	3.412141
	average delta T	9.86	C
	1 year	8766	hours
	energy in year	16	GJ
		4.45	MJ/HDD

location	RSI / m2·K/W	U / W/m2·K	Area / m2	Heat / transfer / W/K	Design / ΔT / °C or K	Heating / power / W	Energy / transfer / MJ	%
R13 walls	2.29	0.44	53.5	23.37	15	351	7271	45%
ceiling	3.35	0.30	48.3	14.44	15	217	4491	28%
R7.5 wall	1.32	0.76	14.9	11.25	15	169	3501	22%
window	0.33	3.00	0.8	2.40	15	36	746	5%
Φ = A × U × ΔT
where Φ is the heat transfer in watts,
U is the thermal transmittance,
ΔT is the temperature differential across the structure,
A is the area in square metres.
https://en.wikipedia.org/wiki/Thermal_transmittance